## Table_12_Technical_PQ
Technical Parameter | Sreepur-1 F5 (Best Technical) | Sreepur-7 F1 (Worst Technical) | Absolute Performance Variance | Dominant Technical Status
Mean Voltage (kV) | 11.12 | 10.65 | 0.47 | Sreepur-1 F5 Stabilized
Voltage Compliance Rate (%) | 96.84 | 48.9 | 47.94 | Sreepur-1 F5 Superior
Grid Frequency Stability (FSI) | 0.96 | 0.88 | 0.08 | Identical/Stable
Mean Power Factor (Lagging) | 0.91 | 0.72 | 0.19 | Sreepur-1 F5 Compliant
Voltage Harmonics (THDv %) | 2.1 | 4.9 | -2.8 | Sreepur-7 F1 Distorted
Thermal Loading Factor | 0.58 | 0.91 | -0.33 | Sreepur-7 F1 Overloaded

## Table_13_Socio_Technical
Socio-Technical Metric | Sreepur-1 F5 (Best Technical) | Sreepur-7 F1 (Worst Technical) | Operational Impact Delta
Composite CPQI Score (%) | 88.4 | 48.9 | 39.5
Annual Customer Complaints | 14 | 82 | -68
Avg Dispatch Response Time (Min) | 35.2 | 142.4 | -107.2
Grievance Resolution Rate (%) | 96.1 | 61.2 | 34.9
Assigned Cluster Archetype | Cluster 1 (High Quality, Low Complaints) | Cluster 2 (Poor Quality, High Complaints) | Significant Service Quality Divergence

## Table_17_Action_Directives
Quadrant Profile Assignment | Empirical Framework Meaning | Targeted Utility Directive & Action Plan
C1: High Complaint, Good PQ | Complaints originate from billing, customer service response latency, local distribution transformer fuses, or localized meter inaccuracies rather than feeder-wide technical drop. | Investigate non-PQ causes: Conduct commercial audits, streamline billing customer service dispatching, check local LT line connections.
C2: High Complaint, Poor PQ | Severe technical infrastructure degradation causing voltage violations or prolonged outages; directly impacting end-consumers and driving high dissatisfaction. | Immediate engineering intervention required: Execute conductor stringing upgrades, balance phase loads, deploy capacitor banks, and overhaul protection switchgear.
C3: Low Complaint, High PQ | Excellent technical performance with minimal consumer grievance logging. Represents the system benchmark standard. | Establish as institutional benchmark: Document best-practices, replicate operational topology to adjacent networks.
C4: Low Complaint, Poor PQ | Hidden structural risks present (poor voltage profiles or low power factor) combined with an abnormally low public reporting rate or passive consumer zone. | Execute preventive maintenance: Dispatched maintenance teams for field inspection, implement automated remote terminal unit (RTU) loggers, check for communication gaps.